## Slide 1
INSPECTION CASES
Experience state of the art Ultrasound and Infrared technologies Integrated into a single device

## Slide 2
Chart: 
| 1 Lv | 2 Lv | 3 Lv | 4 Lv | 5 Lv | 6 Lv
판매 | 0 | 5 | 3 | 3 | 15 | 1
Kincade Fire Transmission Inspection Project
Chart: 
| Chipped out | Contamination | Flashover | Cracked | Broken | Carbonation | Damaged
판매 | 1 | 7 | 4 | 2 | 2 | 1 | 5
Chart: 
| Insulator | Clamp | Cross arm Brace | Conductor
판매 | 17 | 5 | 1 | 4
Priority Level
Defects
Hardware
Date : 11.04 ~ 11.14 2019
Area : Geyserville, CA
A total of 411 structure were acoustically inspected 26 defects were found
Summary

## Slide 3
Kincade Fire Transmission Inspection Project
Corona Discharge
(Ultrasound)
Location : Geysers 12-Fulton 3/16 between 3/17
/ Conductor- Damaged / PL - 2

## Slide 4
Location : Geysers 12-Fulton 17/70
/ Insulator- Flashover / PL - 3
Corona Discharge
(Ultrasound)
Kincade Fire Transmission Inspection Project

## Slide 5
Corona Discharge
(Ultrasound)
Location : Geysers 12-Fulton 9/40
/ Clamp – No visual defects / PL - 5
Kincade Fire Transmission Inspection Project

## Slide 6
Corona Discharge
(Ultrasound)
Location : Geysers 27-Fulton 1/7
/ Insulator - Cracked / PL - 2
Kincade Fire Transmission Inspection Project

## Slide 7
Distribution Inspection Project
Summary
Date : 03.04 ~ 03.16.2020
Area : Santa Rosa, CA
A total of 3400 structure were acoustically inspected
159 Defects were found

## Slide 8
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ Conductor – Erosion/Arcing / PL - 1
Distribution Inspection Project

## Slide 9
Corona Discharge
(Ultrasound)
Location : Castroville 2013 / 64-11500
/ Transformer Bushing – Damaged, Rusted / PL - 1
Distriution Inspection Project

## Slide 10
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ LP Insulator, Conductor – Corrosion, Erosion / PL - 3
Distribution Inspection Project

## Slide 11
Corona Discharge
(Ultrasound)
Location : Castroville 2013 / 42-11381
/ Conductor – Erosion/Arcing / PL - 1
Distribution Inspection Project

## Slide 12
Corona Discharge
(Ultrasound)
Location : Castroville 2013 11341
/ C.O.S – Cracked / PL - 1
Distribution Inspection Project

## Slide 13
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ Conductor – Flashover / PL - 1
Distribution Inspection Project

## Slide 14
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ Conductor – Erosion / PL - 1
Distribution Inspection Project

## Slide 15
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ Conductor – Corrosion/Flashover / PL - 1
Distribution Inspection Project

## Slide 16
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ LP Insulator – Carbonization, Flashover / PL - 2
Distribution Inspection Project

## Slide 17
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ Suspension Insulator – Cracked / PL - 1
Distribution Inspection Project

## Slide 18
Corona Discharge
(Ultrasound)
Location : Castroville 2013
/ LP Insulator – Cracked / PL - 1
Distribution Inspection Project

## Slide 19
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Conductor – Erosion / PL - 1
Distribution Inspection Project

## Slide 20
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Suspension Insulator – Damaged / PL - 1
Distribution Inspection Project

## Slide 21
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Conductor – Erosion/Arcing / PL - 1
Distribution Inspection Project

## Slide 22
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Conductor – Erosion / PL - 1
Distribution Inspection Project

## Slide 23
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Conductor – Erosion / PL - 1
Distribution Inspection Project

## Slide 24
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ Conductor – Broken tie wire / PL - 1
Distribution Inspection Project

## Slide 25
Corona Discharge
(Ultrasound)
Location : Green Velly 2013 9961-148
/ Clamp – Arcing / PL - 1
Distribution Inspection Project

## Slide 26
Corona Discharge
(Ultrasound)
Location : Green Velly 2013
/ LP Insulator, Tie wire – Flashover / PL - 1
Distribution Inspection Project

## Slide 27
Corona Discharge
(Ultrasound)
Location : Big basin 1101
/ Conductor – Foreign object / PL - 5
Distribution Inspection Project

## Slide 28
Corona Discharge
(Ultrasound)
Location : Big basin 1101
/ Conductor – Vegetation / PL - 5
Distribution Inspection Project

## Slide 29
Corona Discharge
(Ultrasound)
Location : WEST POINT 1101
/ Conductor – Damaged / PL - 1
Distribution Inspection Project

## Slide 30
Corona Discharge
(Ultrasound)
Location : WEST POINT 1101
/ Conductor – Damaged / PL - 1
Distribution Inspection Project

## Slide 31
Corona Discharge
(Ultrasound)
Location : Stanislaus 1720 R1739
/ Conductor – Vegetation / PL - 5
Distribution Inspection Project

## Slide 32
Corona Discharge
(Ultrasound)
Location : Stanislaus 1720 L5495
/ Conductor – Vegetation / PL - 5
Distribution Inspection Project

## Slide 33
Corona Discharge
(Ultrasound)
Location : Stanislaus 1720 L5495
/ Transformer Bushing – Arcing/Vegetation / PL - 1
Distribution Inspection Project

## Slide 34
Thank You
WWW.INSPECO.NET
Email : inspeco@insepco.co.kr
CONTACT US: